GENERAL	1

SECTION INCLUDES	1

Service use	1

shipping, handling and storage	1

WORK BY OTHERS	2

Pricing	2

RELATED SECTIONS	2

STANDARDS	2

SUBMITTALS	2

qualifications	2

warranty	2

PRODUCTS	3

1.	tray cable, general Specification	3

2.	tray cable, type tc, 1/c 4/0, nonshielded	4

3.	tray cable, type tc, 1/C #4AWG, nonshielded	4

4.	tray cable, type tc, 4/c #4AWG, nonshielded	4

5.	tray cable, type tc, 2/c #10AWG, nonshielded	5

6.	tray cable, type tc, 3/c #10AWG, nonshielded	5

7.	tray cable, type tc, 4/c #10AWG, nonshielded, AC Power	5

8.	tray cable, type tc, 4/c #10AWG, nonshielded, CT/PT	6

9.	tray cable, type tc, 12/c #10AWG, nonshielded	6

10.	tray cable, type tc, 12/c #12AWG, nonshielded	6

11.	tray cable, type tc, 4/c #14AWG, nonshielded	7

12.	Switchboard cable, type sis, #14AWG, nonshielded	7

13.	tray cable, type tc, 12/c #18AWG, nonshielded	7

14.	tray cable, type tc, 2/c #10AWG, shielded	8

15.	tray cable, type tc, 4/c #10AWG, shielded	8

16.	tray cable, type tc, 12/c #10AWG, shielded	8

17.	tray cable, type tc, 12/c #12AWG, shielded	9

18.	tray cable, type tc, 12/c #18AWG, shielded	9

19.	tRAY CABLE, type pltc, 2/c #20AWG, Sunlight Resistant, shielded	9

20.	accessories	10

EXECUTION	10

GENERAL

SECTION INCLUDES

This specification includes the minimum requirements for various types of cable, tray-rated cable (NEC Type TC and Type PLTC).  These are cable types that Farmington Electric Utility System (FEUS) buys and stocks in their warehouse.

Service use

The cables shall be installed indoors and outdoors in cable tray and other raceway in various locations in and around Farmington, New Mexico, in the FEUS service area.

shipping, handling and storage

The cable shall be handled and stored in accordance with the MANUFACTURER’s recommendations until received by the PURCHASER.

WORK BY OTHERS

The following work shall be done by others:

Offloading and receiving at FEUS warehouse.

Pricing

Prices shall be quoted FOB to the FEUS yard.

RELATED SECTIONS

None.

STANDARDS

The equipment shall be designed, manufactured and tested in accordance with the latest applicable standards to include, but not be limited to:

American Society of Testing and Materials (ASTM International).

Underwriters Laboratories, Inc. (UL).

Institute of Electrical and Electronics Engineers (IEEE).

Insulated Cable Engineers Association (ICEA).

National Electrical Manufactures Association (NEMA).

National Electric Code (NEC).

National Fire Protection Association (NFPA).

SUBMITTALS

All submittals shall be sent to the PURCHASER for review and approval.  Submittals shall be electronic and distribution shall be as follows:

Send electronic files to:

Farmington Electric Utility System

Attn. Electric Utility Warehouse

101 Browning Parkway

Farmington, NM   87401

Manufacturer’s catalog data.

qualifications

MANUFACTURER

The MANUFACTURER shall be a company having manufactured the proposed cable type for a period of at least five (5) years.

warranty

The MANUFACTURER shall warrant that the cable meets all pertinent specifications and requirements.

PRODUCTS

- tray cable, general Specification

    - Approved Manufacturer

      - Okonite

      - Southwire

      - Belden

      - General Cable

      - Service Wire Co.

      - Or approved equal.

    - The cable furnished must be manufactured no more than 24 months prior to receipt of order.

    - The conductors and cable shall be round in shape.

    - Strand copper conductor: ASTM 8, Class B or C.

    - AWG designation.

    - Insulation for #14awg and larger must be rated at a minimum of 600V with continuous operation at 90°C in wet or dry conditions, unless otherwise specified

    - Jacket must be UV resistant, Oil resistant, and Flame resistant.

    - ICEA Method 1

      - Table E1; 1-Black, 2-White, 3-Red, 4-Green

      - Table E2; 1-Black, 2-Red, 3-Blue, 4-Orange, 5-Yellow, 6-Brown, 7-Red/Black Stripe, 8-Blue/Black Stripe, 9-Orange/Black Stripe, 10-Yellow/Black Stripe, 11-Brown/Black Stripe, 12-Black/Red Stripe

    - Reel size shall be no greater than 42” and provide the minimum number of reels for the length ordered unless otherwise specified.

- tray cable, type tc, 1/c 4/0, nonshielded

    - FEUS Stock Number: Not Stocked

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Color code: Determined on order (Black, Red, or White)

      - Deliver on 1000-foot reels

- tray cable, type tc, 1/C #4AWG, nonshielded

    - FEUS Stock Number: Not Stocked

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Color code: Determined on order

      - Deliver on 1000-foot reels

- tray cable, type tc, 4/c #4AWG, nonshielded

    - FEUS Stock Number: Not Stocked

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E1

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 2/c #10AWG, nonshielded

    - FEUS Stock Number: 280 030 7002

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 3/c #10AWG, nonshielded

    - FEUS Stock Number: 280 030 7025

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: Black, White, Green

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 4/c #10AWG, nonshielded, AC Power

    - FEUS Stock Number: 280 030 7030

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code:  ICEA Method 1, Table E1

      - Deliver on

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 4/c #10AWG, nonshielded, CT/PT

    - FEUS Stock Number: 280 030 7003

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code:  ICEA Method 1, Table E2

      - Deliver on

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 12/c #10AWG, nonshielded

    - FEUS Stock Number:  280 030 7028

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 12/c #12AWG, nonshielded

    - FEUS Stock Number: 280 030 7027

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 4/c #14AWG, nonshielded

    - FEUS Stock Number: 280 030 7026

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

      - Approved

        - Belden C04142G

- Switchboard cable, type sis, #14AWG, nonshielded

    - FEUS Stock Number: 280 030 70##

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

        - 90oC Wet/Dry

      - Conductor

        - Tinned Copper

      - Color - Gray

      - Deliver on:

        - 500-foot reels

- tray cable, type tc, 12/c #18AWG, nonshielded

    - FEUS Stock Number: 280 030 7005

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2, RHW-2, or THHN/THWN

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 2/c #10AWG, shielded

    - FEUS Stock Number: 280 030 7043

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Shield

        - Helically applied Cu tape, 5 mil annealed or 2 x 2mil, minimum 10% overlap

      - Drain wire

        - Stranded copper

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 4/c #10AWG, shielded

    - FEUS Stock Number: 280 030 7040

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Shield

        - Helically applied Cu tape, 5 mil annealed or 2 x 2mil, minimum 10% overlap

      - Drain wire

        - Stranded copper

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 12/c #10AWG, shielded

    - FEUS Stock Number: 280 030 7044

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Shield

        - Helically applied Cu tape, 5 mil annealed or 2 x 2mil, minimum 10% overlap

      - Drain wire

        - Stranded copper

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 12/c #12AWG, shielded

    - FEUS Stock Number: 280 030 7041

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2

      - Shield

        - Helically applied Cu tape, 5 mil annealed or 2 x 2mil, minimum 10% overlap

      - Drain wire

        - Stranded copper

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tray cable, type tc, 12/c #18AWG, shielded

    - FEUS Stock Number: 280 030 7042

    - Characteristics:

      - Insulation

        - 600V

        - XHHW-2, RWH-2, or THHN/THWN

      - Shield

        - Helically applied Cu tape, 5 mil annealed or 2 x 2mil, minimum 10% overlap

      - Drain wire

        - Stranded copper

      - Jacket

        - PVC

      - Color code: ICEA Method 1, Table E2

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- tRAY CABLE, type pltc, 2/c #20AWG, Sunlight Resistant, shielded

    - FEUS Stock Number: 280 030 7010

    - These preapproved products only:

      - Manhattan Wire, #M9520010

      - Beldon #1033A

      - Isotec (Manufacturer provide product number)

    - Characteristics:

      - Insulation

        - 300V

        - 105°C

      - Drain wire

        - Stranded copper

      - Deliver on:

        - 500, 1000, 2500, or 5000-foot reels

- accessories

    - None.

EXECUTION

- NOT USED

END OF SECTION