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GENERAL SPECIFICATIONS
CHAPMAN CAMPGROUND NORTH WATERLINE REPLACEMENT
June 7th, 2026
SCOPE OF CONTRACT
This project includes excavating, demolishing and reconstructing sections of the north portion of the public water system at the Chapman Campground.  The north part of the system has historically had problems with rust and iron contamination due aging of the infrastructure.
Water system and line replacement will take place in portions north of the bridge over the Frying Pan River including Area A; Area B; Area C; Loop E; and all system lines between and supplying these areas.  The attached figure details segments that are to be replaced.
Work will include excavation and disposal of the current system lines, hydrants and drain lines and all associated demolition materials; placement of bedding material; installation of new 1-inch HDPE water lines; installation of new hydrants including shutoff valves, drainage grates and drain lines; and construction of ADA/accessible gravel paths and pads at each hydrant.
New waterlines will be installed in the same locations/alignments as the current lines.  It is estimated that the burial depth of the existing lines is approximately 3 to 4 feet.
Pad construction using concrete in place of gravel will be considered as an Option Item.

Bid Includes: Quantities associated with these options are identified in the Schedule of Items.
General Conditions 
Mobilization/demobilization 
Waterline Replacement
E Loop “T” to Site 26 Hydrant—695 feet
Loop E Line to Site 36 Hydrant—425 feet
End of fill station to Area B Hydrant—245 feet
Area B Hydrant to Area C Hydrant—505 feet
Area B Hydrant to Area A Hydrant—275 feet
Additional Item?
Water Hydrant and Curb Valve Installation
0. Replacement of 7 hydrants (Areas A, B, C; E Loop Sites 26 and 36; D Loop; and Host Site)
Installation of 5 “isolation” curb stop shutoff valves (Area C; Area B just after the D Loop hydrant; Area A; E Loop after the “T”; and the Host Site)
Additional Item?
Waste Disposal
Optional Items:
Construct concrete pads at each hydrant (7)
Additional Item?

Work includes:
0. Item:
Scope/Description

PROJECT LOCATION 
The project is located approximately 60 miles east of Basalt, CO on County Road 104 (“Frying Pan Road”, Eagle/Pitkin Counties), see attached location map.
SITE INFORMATION AND LIMITATIONS
The following site conditions are considered incidental to the contract, and the contractor will not be paid directly for any of the following items:
The campground (“construction site”) will be closed to the public during construction. Camping will be permitted during construction.
The Contractor will provide all materials and labor necessary for erosion protection during construction activities.  The Contractor will be required to submit an erosion control plan and receive approval from the Forest Service, in writing, prior to the beginning of construction. 
All construction equipment shall be pressure-washed before entering National Forest System lands.  The removal of mud and debris from treads, tracks and undercarriage, with emphasis on axles, frame, cross-members, motor mounts, and underneath steps, running boards, and front bumper/brushguard assemblies will be required.  The purpose is to reduce or eliminate the transportation of noxious weeds, which is required by Federal and State regulations. Construction equipment shall be inspected on a trailer prior to offloading the equipment.  Contractor shall give the Forest Service a minimum of 72 hours (3 business days) notice prior to needing inspection.
Utilities are not available at the site for construction purposes, however potable water may be available on site.
Vault toilet facilities are available at the site for contractor use, and if used shall be cleaned and pumped at the end of the construction at the expense of the Contractor.
Trash/dumpster service will not be available during construction and Contractor will be responsible for removal of all trash and personal waste.
WORK CAMPS, STAGING AND STORAGE AREAS
Areas for staging operations and storage of materials shall be approved by the Forest Service.  The Contractor must request approval from the Forest Service to stage trailers (work or housing) on site.
Camping will be allowed onsite per Forest Service approval.
INSPECTION OF WORKSITE
The contractor is responsible for taking the necessary steps to accurately inspect, investigate and verify the general project details and quantities presented in this Scope of Work that can affect the work or its cost without additional expenses to the Government.
START DATE
September 9th, 2026
CONTRACT TIME
Base Bid/Optional Items (if awarded): 30 Calendar Days
Other 

